"ELECTRIC NETWORKS OF ARMENIA"       CJSC

AUTOMATED CONTROL SYSTEM

FOR TECHNOLOGICAL PROCESSES, AND TELEMECHANIC SYSTEMS

TERMS OF REFERENCE

2025

CONTENT

1.	GENERAL INFORMATION 	4

2.	GOALS AND OBJECTIVES FOR  CREATING AN AUTOMATED SYSTEM 	4

2.1. Goals for creation of  ACS TP & TMS	4

2.2 Purpose of  ACS TP & TMS	4

3.	DESCRIPTION OF FACILITIES TO BE AUTOMATED	5

4.	  REQUIREMENTS FOR THE AUTOMATED SYSTEM 	6

4.1	Requirements for  ACS TP & TMS structure	6

4.2	SCADA Software Requirements	6

4.2.1.      General requirements    	6

4.2.2.Requirements for the functions of the basic SCADA control system.	10

4.2.3. Detailed requirements for SCADA architecture	17

4.3	Requirements for TM Boxes	17

4.4	Requirements for the programmable controller	19

4.5	Requirements for modules RS, TM 	21

4.6	Requirements for communication channels 	22

4.7	Reliability Requirements	22

4.8	Information Security Requirements 	23

5.	COMPOSITION AND CONTENT OF WORKS ON CREATING THE AUTOMATED SYSTEM 	31

6.	  PROCEDURE FOR DEVELOPING THE AUTOMATED SYSTEM	32

6.1	List of documents and baseline data for the development 	32

6.2	List of documents to be submitted upon completion of work 	32

6.3	Warranty Requirements	32

7.	 PROCEDURE FOR CONTROL AND ACCEPTANCE OF THE AUTOMATED SYSTEM 	32

7.1	Preliminary testing 	32

7.2	Trial operation 	32

7.3	Acceptance testing	32

8.	REQUIREMENTS FOR THE COMPOSITION AND CONTENT OF WORKS TO PREPARE AN AUTOMATION FACILITY FOR COMMISSIONING THE AUTOMATED SYSTEM 	33

9.	DOCUMENTATION REQUIREMENTS	33

10.	REFERENCE SOURCES FOR DEVELOPMENT	33

ANNEX 1. Facilities connected to SCADA system of CJSC «ENA»	34

ANNEX 2. Short list of information  received from automation facilities of  CJSC «ENA»	35

List  of Acronyms

| ARA | Automatic reserve activation |
| --- | --- |
| AWP | Automated workplace |
| ACS TP | Automated Control System for Technological Processes |
| VCB | Vacuum circuit breaker |
| BBD | Busbar disconnector |
| GN | Grounding knife |
| MOP | Maximum overcurrent protection |
| LBP | Logical bus protection |
| CC | Current cutoff |
| SPGF | Single phase to ground fault |
| CBFBD | Circuit breaker failure backup device |
| VT | Voltage transformer |
| DB | Database |
| UPS | Uninterruptible power supply |
| LAN | Local Area Network |
| MFMT | Multifunctional measuring transducer |
| RP&A MPT | RP&A Microprocessor terminal |
| RRI | Regulatory and reference information |
| ODS | Operational dispatch service |
| ODC | Operational dispatch control |
| PQI | Power quality indicators |
| SW | Software |
| SS | Substation |
| EER | Emergency Event Registration |
| RP&A | Relay protection and automation |
| SP | Switching point |
| SG | Switchgear |
| ToR | Terms of reference |
| TM | Telemetry |
| CTM | Current telemetry |
| TM | Telemechanics |
| TSS | Transformer substation |
| RS | Remote Signaling |
| RC | Remote control |
| CR&TS | Central receiver and transmitter station |
| EM RP&A | Electromechanical RP&A |
| DMS | Distribution management system |
| EMS | Energy management system |
| OMS | Outage management systems |
| SCADA | Supervisory Control and Data Acquisition |
| ESMS | Electricity Smart metering systems |
| RDMT | Rapid deployment mobile teams |
| SHC | Software-hardware complex |
| PTL | Power transmission line |
| CDS | Central Dispatch Service |

# GENERAL INFORMATION

Full name of the system: AUTOMATED CONTROL SYSTEM for TECHNOLOGICAL PROCESSES, and TELEMECHANIC SYSTEMS for "ELECTRIC NETWORKS OF ARMENIA" CJSC »

Brief name of the system: ACS TP & TMS for CJSC «ENA»

Name and details of the Customer's Company:

"Electric Networks of Armenia" Closed Joint Stock Company

Legal address: 127Armenak Armenakyan street, Nork-Marash district, 0011 Yerevan, Armenia

# GOALS AND OBJECTIVES FOR CREATING AN AUTOMATED SYSTEM

# 2.1. Goals for creating of ACS TP & TMS

- to increase  the efficiency of operation and management of substations across the entire technological complex of "ENA" CJSC in normal and abnormal (including emergency) modes;

- to ensure the required quality indicators of electricity and the level of service for electricity market participants when solving problems of transmission, transformation and distribution of electric power;

- to reduce the accident rate, reduce damage from accidents and reduce the time for eliminating  accidents;

- to increase the reliability and safety of operation, improve the operational maintenance of the main and auxiliary technological equipment, and to reduce the cost of repair work;

- ensure systemic and complex integration, including:

- relay protection and automation systems and emergency automated control systems;

- automated technological process control systems;

- telemechanic systems;

- emergency event registration systems;

- PQI control systems;

- communication systems;

- information interaction with automated metering systems and other external subsystems;

- reduction of operating costs of substations;

- increasing the level of information and general security of the technological complex.

# 2.2 Purpose of  ACS TP & TMS

- measurement of electrical and technological parameters and their conversion to digital format;

- acquisition of analog and discrete data on the technological process and equipment status using periodic polling and/or sporadic changes in the signal/parameter with using apertures for telemetry;

- transfer of data from the controlled facility to the regional and central management levels;

- remote dispatch control of the technological process and monitoring of the equipment condition;

- prevention of accidents, monitoring the occurrence and development of emergency situations;

- remote reading of oscillograms of emergency processes;

- archiving process progress data, maintaining a historical archive;

- technical accounting at electrical and technological parameters;

- providing a human-machine interface with the execution of requests for data in various formats, visualization of the automation facilities and the technological process, maintaining the event logbook, emergency and warning alarms, generating trends and oscillograms of ongoing processes, and control by dispatcher commands;

- data registration and recording on storage media with the possibility of subsequent print-out;

- restricting access to data through a password system and blocking unauthorized access;

- automatic data saving during power outages;

- time unification of devices, and assigning time stamps to process parameters;

- data exchange between control and monitoring subsystems;

- automatic functional diagnostics of process equipment and elements of technical and software support for ACS TP & TMS.

# DESCRIPTION OF FACILITIES TO BE AUTOMATED

All work must be executed by the Contractor on a turnkey basis.

The Terms of reference has been drawn up for automation of the following distribution network facilities:

- 110 kV substations

- 35 kV substations;

- switching points 6 (10) kV;

- transformer substations 6 (10) kV.

- 110 kV substations

  - Substations with operating ACS TP (Type 1.1)

In 2013-2014, the CHINT company (China) carried out modernization of 17 110kV substations. These substations are equipped with digital microprocessor relay protection and automation systems  RP&A and an automated process control system  ACS TP is organized using intelligent controllers connected to a local SCADA, which allows receiving and processing signals, as well as implementing control from SS AWP.

Features:

• Signals from the RP&A MPT 110 kV and the ACS TP controllers are sent to the local SCADA via the proprietary protocol of the «Sifang» company (China).

• Signals from the RP&A MPT 10 kV are transmitted in the Modbus protocol via the CAN interface.

• Data transfer from the ACS TP to control centers is not currently performed;

• Only local control is performed from the SS AWP.

Requirements:

- Install modern communication controllers to ensure the organization of data transmission from RP&A MPT and ACS TP controllers to the dispatch centers of «ENA» CJSC.

- Organize direct polling of RP&A terminals and ACS TP controllers (both 110 kV and 10 kV) by new communication controllers directly via standard open protocols.

- When upgrading ACS TP, the volume of collected information remains unchanged.

- If necessary (if the controller does not have such capacities), to receive some basic signals (for example, phase voltage, position of the BBD GN, etc.), additional equipment shall be installed by the Contractor.

- Replace existing AWPs with new ones with installation a modern local SCADA without a database, operating autonomously from the SCADA CDS.

- Eliminate the possibility of simultaneous control of the facility from SS AWP and the CDS  AWP.

If it is impossible to integrate the existing controllers into the new ACS TP system due to their malfunction or inoperability, ENA» CJSC will replace them by itself.

.

  - . Substation with ACS TP with digital terminals RP&A (Type 1.2)

There is no ACS TP in these substations, however there are digital RP&A terminals installed (e.g. Ekra 2502, Ekra 2704 – in four substations, Areva P127 P543 – in one substation, and Орион РТЗ (Orion RPS) in one substation).

Requirements:

• Develop and introduce a new ACS TP.

• Organize data acquisition in accordance with Annex 2.

• Install the SS AWP, with the installation of a modern local SCADA without a DB, operating autonomously from the SCADA CDS.

• Eliminate the possibility of simultaneous control of the facility with the SS AWP and the AWP CDS.

• Ensure the integration of all digital RP&A devices and the collection of the maximum amount of information from them.

• Control the circuit breakers through the digital RP&A terminals.

• Control the BBD and the GN if technically feasible, if necessary, by installing the necessary equipment.

1.3. Substations without ACS TP with electromechanical devices RP&A (Type 1.3)

There are no digital RP&A in these substations.

Requirements:

- Develop and introduce a new automated process control system (ACS TP), taking into account that in the near future these substations will be reconstructed and the installed equipment should be used in the reconstructed substations with minimal additions.

- Organize the collection of information in accordance with Annex 2.

- Install the SS AWP, with the installation of a modern local SCADA without a DB, operating autonomously from the SCADA CDS.

- Eliminate the possibility of simultaneous control of the facility with the SS AWP and the CDS AWP .

- Information is collected via discrete inputs, including information on the operation of the relay protection and automation system RP&A.

- Control of the main circuit breakers shall be made directly by setting the remote control selection key on “local/remote” mode.

- Control the BBD and GN shall be performed if technically feasible, and if necessary, by additionally installing the required equipment.

  - Subscriber substations (Type 1.4)

The Contractor shall not install any ACS TP (TM) devices at subscriber substations within the framework of this project. Solutions for equipping with ACS TP (TM) shall be implemented by ENA» CJSC. In turn, the Contractor shall ensure reception of data from the ACS TP (TM) in the newly created SCADA CDS and branches of ENA» CJSC.

The ACS TP (TM) for 110 kV substation to be created must be implemented using a three-tier architecture:

• Lower level – the level of controllers and existing digital terminals of the relay protection and automation system RP&A, performing the collection and transmission of information to higher levels;

• Middle level – the level of communication controllers, providing the collection, aggregation and transmission of information to the ENA» CJSC dispatch centers;

• Upper level – the level of local SCADA (SS AWP) independent of the SCADA to be installed in  CDS. The upper level performs the functions of displaying current information, manual substitution, and is the main means of controlling the primary equipment of the substation.

- 35 kV substations

  - Substations with implemented ACS TP (Type 2.1)

There are this Type of substations.

  - Substations with ACS TP with digital terminals RP&A (Type 2.2)

There are no ACS TP in these Substations, however there are digital RP&A terminals installed (mainly Орион РТЗ).

Requirements

- Develop and introduce a new automated process control system (ACS TP).

- Organize the collection of information in accordance with Annex  2.

- Ensure the integration of all digital RP&A devices and the collection of the maximum amount of information from them.

- Install the SS AWP, with the installation of a modern local SCADA without a DB, operating autonomously from the SCADA CDS .

- Eliminate the possibility of simultaneous control of the facility with the SS AWP and the CDS AWP .

- If necessary (if the controller does not have such capacities), to receive some basic signals (for example, phase voltage, position of the BBD GN, etc.), additional equipment shall be installed by the Contractor.

- Control of circuit breakers to be performed via digital terminals RP&A.

- Perform control of the and BBD and GN = BBD и GN if technically possible, if necessary, install the necessary equipment.

  - Substations without ACS TP with electromechanical devices RP&A (Type 2.3)

There are no digital RP&A in these substations.

Requirements:

- Develop and introduce a new automated process control system (ACS TP), taking into account that in the near future these substations will be reconstructed and the installed equipment should be used in the reconstructed substations with minimal additions.

- Organize the collection of information in accordance with Annex  2.

- Information is collected via discrete inputs, including information on the operation of the relay protection and automation system RP&A.

- Control of the main circuit breakers shall be made directly by setting the remote control selection key on “local/remote” mode

- Perform control of the and BBD and GN if technically possible, if necessary, install the necessary equipment.

  - Subscriber substations (Type 2.4)

No ACS TP devices shall be installed at subscriber substations within the framework of this project. If necessary, “ENA» CJSC shall independently organizes the collection and transmission of a minimum volume of telemetric information in accordance with the technical conditions of “ENA» CJSC

The ACS TP (TM) for 35kV substation to be created, must be implemented using a three-tier architecture:

• Lower level – the level of controllers and existing digital terminals of the relay protection and automation system RP&A, performing the collection and transmission of information to higher levels;

• Middle level – the level of communication controllers, providing the collection, aggregation and transmission of information to the ENA» CJSC dispatch centers;

• Upper level – the level of local SCADA (SS AWP) independent of the SCADA to be installed in  CDS. The upper level performs the functions of displaying current information, manual substitution, and is the main means of controlling the primary equipment of the substation.

- Switching points (10) kV

  - SP= РП with implemented ACS TP (Type 3.1)

There are no SP of this type.

  - SP without ACS TP

    - SP without ACS TP with “Lyutik” type RP&A MPT (Type 3.2.1)

On these SPs, the primary and secondary equipment was reconstructed, and RP&A MPT of the “Lyutik” type with the ability to transmit information in digital protocols were installed.

Features:

- RP&A MPT"Lutik" are not connected to voltage circuits due to the peculiarities of their functionality. Therefore, it is possible to transmit only current measurement data from them.

Requirements:

- Develop and introduce a new automated process control system (ACS TP).

- Organize the collection of information in accordance with Annex  2.

- •	Ensure the integration of all digital RP&A devices and the collection of the maximum amount of information from them.

- Install digital measuring converters at the input cells of SG = РУ-6(10) kV, also connected to voltage circuits.

- Control of circuit breakers to be performed via digital terminals RP&A.

The volume of teleinformation collected by the ACS TP (TM) is limited to the information that can be collected from the RP&A MPT. Within the framework of this title, the installation of additional devices in 6-10 kV cells is not envisaged, with the exception of measuring converters in input cells.

    - SP without ACS TP with RP&A MPT of «ТОР-200»/ «ТОР-150» type (Type 3.2.2).

The requirements are similar to section 3.2.1, except for the installation of measuring transducers.

When implementing, take into account that the reconstruction of part of the SP with the replacement of primary and secondary equipment with using RP&A MPT of the TOR-200 or TOR-150 type is planned for 2025. Carry out the organization of the ACS TP on these SPs upon the completion of their reconstruction in accordance with the requirements of Section 3.2.

The volume of teleinformation collected by the ACS TP (TM) is limited to the information that can be collected from the RP&A MPT. Within the framework of this title, the installation of additional devices in 6-10 kV cells is not envisaged, with the exception of the installation, if necessary, of digital converters connected to the voltage circuits of the SP inputs.

  - SP without ACS TP with electromechanical devices RP&A (Type 3.3)

These SPs do not have digital RP&A devices, and the primary and secondary equipment has not been reconstructed. Reconstruction of these RPs is planned to be performed after completion of the current stage of work.

Requirements:

- Develop and introduce a new automated process control system (ACS TP), taking into account that in the near future these SPs will be reconstructed and the installed equipment should be used with minimal additions in the reconstructed SPs.

- Organize the collection of information in accordance with Annex  2.

When implementing, take into account that the ACS TP equipment installed at facilities of this type must be:

• Ready for integration of digital RP&A terminals, which will be implemented during subsequent reconstruction.

• Capable of providing remote control functions through new RP&A terminals after their installation.

The installation of additional TM equipment is not envisaged at these facilities.

4.2. TSS/Facilities without ESMS (Type 4.2)

To perform the work specified in this section it is necessary to install a controller that will have the appropriate number of dry contacts to ensure that signals of the presence or loss of voltage from the input and/or 0.4 kV directions are sent to the main server, as well as data from the meters installed in the substation.

Introduction of the ACS TP & TMS в CJSC «ENA» systems shall be carried out in the following phases:

Phase 1.

- High-voltage substations in Yerevan:

  - 25 units of 110 kV SSs (of which 2 customer substations,

  - 18 units of 35Kv SSs,

  - 92 reconstructed 6(10) kV SPs,

  - 58 TSSs in the Small center of Yerevan of

- 41 SPs subject to reconstruction in 2025.

- 500 facilities selected for voltage presence monitoring.

Phase 2.

      - Yerevan in full:

  - the remaining SPs – 40 units,

  - 6(10)/0.4kV TSS – about 2 000 units.

The facilities with old, outdated equipment must be included in the ACS TP & TMS system by providing the minimum possible RS.

The above provision shall not limit the Contractor from starting works of other phases prior to completion of the previous ones. However, before starting the work on the first stage, the Contractor must meet the requirements specified for 110kV substations of type 1.1 (Sifang terminals) using the example of a substation selected by "ENA" CJSC.

More detailed information on the scope of work and the degree of readiness of the facilities can be found in Annex 1.

The terms of reference require importing single-line diagrams in full in AutoCad format into SCADA or drawing them in SCADA for all 6–110 kV facilities of ENA CJSC, including those from which data is not received by SCADA due to their technical unavailability. Non-automated elements of single-line diagrams must be displayed and have the ability to manually enter values ​​with subsequent archiving of these data in the SCADA database.

# REQUIREMENTS FOR THE AUTOMATED SYSTEM

# Requirements for the structure of the dispatch control

ACS TP & TMS must have a three-level structure  of dispatch control:

a) first level: the level of  “ENA” CJSC operational and dispatch control;

b) second level:  the level of operational and dispatch services of the “ENA” CJSC branches;

c) third level: the level of the distribution network facilities (SS, SP, TSS).

At the 35 kV substation, distribution substation and transformer substation, dispatching at the third level of dispatch control is carried out by an operational mobile team using a mobile AWP= ARM, which acts as a client of the SCADAof the  “ENA” CJSC dispatch center.

At 110 and 35 kV substations, dispatching at the third level of dispatch control is performed on a newly installed local AWP  operating independently of the SCADA dispatch center  of “ENA” CJSC

# SCADA Software Requirements

The main element of the ACS TP & TMS shall be  UDC and UDS ODC  and ODS level SCADA software.

The software must have a user-friendly interface, whichshall be in Russian language; in the future, together with specialists from CJSC «ENA» at least the electronic operational journal must be translated into Armenian.

It will be necessary to provide for annual software maintenance, which will include Consultation with the relevant specialist(s) during the warranty and post-warranty period in 24/7 mode, where it is impossible to resolve the problems by “ENA” CJSC specialist, also, performing work initially using a remote connection to SCADA software, and if it is impossible to solve problems remotely, to do it on-site during business hours.

Following the stated warranty period date, the SCADA ACS TP & TMS systems shall become the property of ENA” CJSC without any additional fees for the annual license. Moreover, it is possible that as a result of negotiations with the organization implementing the software, this software shall gradually become the property of ENA” CJSC.

# Requirements for a price proposal for SCADA

# The price proposal under these terms of reference shall consist of the following components:

a) cost of software with prices for AWP, number of clients, number of web servers, adding new tags (objects), etc.,

b) the annual cost for renewing the software license (if any),

c) the annual cost of software maintenance (updates, problem solving, etc.), if any,

d) cost of server equipment, computer equipment and Video Walls (мнемощит) installed on the first and second levels, or the cost of similar equipment (in details),

d) detailed cost of equipment installed at the facilities (ТМ panel, controller, UPS, etc.),

e) cost of installation works,

g) cost of adjustment work,

հ) cost of subsequent training of personnel ,

i) the cost of further technical maintenance of the system, excluding the cost of spare parts (if the Contractor agrees to continue servicing the system)

յ) other expenses (indicating the item of each expense ).

# General requirements

SCADA must implement a full range of tasks and function as a full-fledged distribution network management system ensuring automation of all operational and most non-operational functions, including:

- 	shift handover/acceptance;

- 	switching control;

- 	management of emergency response, eliminating erroneous switching;

- 	maintaining a set of operational documentation (including the daily report, the logbook of deviations from the normal scheme, the logbook of equipment damage, operational logbook, оперативный журнал, logbook of work permits and orders, etc.);

- provision of assistance in decision-making in emergency and daily routine (planned) situations. Under this requirement the software must be able to perform automatic switching during an emergency event by automatically performing a multi-level analysis of the emergency in cases pre-defined by the dedicated user. Additionally, after detection of a damaged/suspicious/ section by means of analysis, the software must prompt the duty personnel of the sequence of possible shutdowns in order to ensure connection of substations on the non-emergency section as promptly as possible. In this case, if the emergency section has already been identified by the dispatching personnel, the software must offer the optimal version of the mnemonic diagram taking into account the parameters of the data and adjacent nodes entered into the program (length of cable/overhead lines, cross-section, transformer power, load at the time of the emergency, etc.);

- in daily /normal mode calculation of optimal modes and presentation of the optimal scheme to the dispatcher;

- display the location of operational staff and the nearest available operational staff to the accident site, etc.

- the complex must provide a full cycle of control of the electrical network equipment operated by the Network Company.

SCADA client worksplaces can be installed both on workstations and on mobile/portable platforms (Web-SCADA, EnergoDispatcher- ЭнергоДиспетчер). The capacities of the AWP can be used by the RDMT and HVLS personnel, including access to the album of diagrams, viewing their operational status, maintaining logbooks, viewing/executing switching programs.

The principles of constructing the SCADA information model must correspond to the methods of describing control objects, formulated in the international standards IEC 61970 and 61968 (CIM – Common Information Model). Export of information in the CIM XML format in accordance with IEC 61970 and 61968.

Upon the readiness of “ENA” CJSC to introduce it, SCADA must allow the system functionality to be expanded starting from manual maintenance of the mnemonic diagram or logs, ending with automatic registration of technological failures, generation of reports and sending to the addressees.

SCADA shall use a graphical system performing wide range of functions in the choice of design of operational network diagrams, high-quality graphical representation of individual elements, ensuring excellent characteristics when displaying large volumes of graphical information for shared screen display systems.

SCADA must have a set of characteristic features for application in electrical distribution networks, including:

- focus on working with large schemes/diagrams. Performance graphics;

- 	support for geographical representation of network diagrams;

- 	the ability to “manually” maintain a mnemonic diagram – not only of switching devices, but also of arbitrary states and parameters of equipment and events, the ability to install portable grounding, posters and signs, RDMT symbols, etc.;

- 	wide range of options for working with a shared screen (control, monitoring of video walls);

- 	a developed system for maintaining electronic operational and technological logs;

- 	the ability to form a compact representation of the diagram to ensure space savings on display devices and ease of perception while maintaining information content;

- 	the ability to flexibly customize graphic display symbols according to the Customer’s standards;

- 	the ability to export and import multiple graphic formats;

- 	checking the admissibility of performing operations based on the switching rules in electrical installations for the current state of the circuit;

- 	implementation of operational and technological tasks at the level of the power facility and the electrical network, including management of repairs, technological failures, consumer appeals and localization of damage, management of the RDMT, prompting the dispatcher with information about the located of RDMT at the accident site;

- 	standard solutions for integration with databases of arbitrary structure;

- 	open architecture – the ability to integrate the scheme with specific tasks (consumer accounting databases, calculation of modes, etc.), support export and import of data in CIM XML format in accordance with IEC 61970 and 61968.

.

Requirements for Video Wall

- Video Wall shall be installed in Central Control Service of  “ENA” CJSC ,

- The Video Wall  must provide the display of the current mnemonic diagram and have the ability to represent and display any SCADA data specified in this terms of reference,

- The Video Wall must have a warranty period of at least 5 years in case of LED burnout and other technical malfunctions,

- The Video Wall must have a modular (mosaic) structure, with the ability to quickly replace any failed module,

- When working with static objects, the Video Wall modules must ensure image deflection to avoid rapid failure (burnout) of the LEDs,

- The cover layer of the Vide wall modules must be made of a matte material.

Within the framework of this technical specification, the Contractor may propose an alternative to the mnemonic shield, specifying the separate cost of the alternative option.

Requirements for the central receiver and transmitter station

Requirements for the CR&TS, according to:

SO 34.48.159-2004

GOST 26.205-88

GOST 14254-15 ( IEC 60529:2013)

GOST 15543.1-89

GOST 18145-81

GOST 23675-79

GOST IEC 60950-1-14

GOST R IEC 60870-2-2-01

GOST R IEC 60870-5-101-06

GOST R IEC 60870-5-104-04

The software for CR&TS must perform the functions of information exchange  and must be designed for operation as part of the SHC ACS TP. The software for CR&TS  must collect, process and transmit telemetry information received via communication channels. The CR&TS as part of the SHC system must have the capacity to be perform both on the basis of SCADA application software as part of a dedicated CR&TS server and as part of the main SCADA server.

Requirements for the information exchange  function include:

a.	Reception and transmission of telemechanical information via various communication channels in various exchange protocols:

- 	independent choice of information exchange  protocol for each communication channel;

- shall support standard protocols based on GOST R IEC 60870-5-101/103/104, IEC 61850; OPC DA 2.0;

- the ability to expand the library of supported protocols;

- 	to monitor the availability/accessibility of software and hardware for data exchange  of information systems and communication channels, it shall be possible to collect diagnostic signals via the SNMP protocol with subsequent retransmission in the IEC 60870-5-104 protocol,

- 	the information must contain the time stamps of the last change and quality attributes, including additional ones (manual input, reason for setting the fault attribute, calculated value indicator, etc.);

b. 	retransmission of telemechanical information to other power system facilities;

c. 	conversion of telemechanical exchange protocols;

d. 	formation of data in a real-time database (storage of current operational information);

e. 	exchange of telesignals (TS), including multi-position ones;

f. 	exchange of parameter values;

g. 	exchange of remote control (RC) commands;

h. 	independent setting of exchange modes (sporadic, cyclic/periodic, on request) for each channel;

i. 	recording the moment of data receipt and monitoring the loss of information:

- 	via data channel;

- - via controlled points (CP);

- 	in case of multiple retransmission – by  individual information object parameters;

j. 	storing current values and states of information exchange ;

k. 	conversion of format, address and status information during retransmission.

l. 	providing the following modes of information transfer:

- 	RS and CTM (current telemetry) must be transmitted when the value (information) changes; in this case, a change in the quality attribute must also be considered as a change in information;

- transmission of the full volume of RS and CTM upon request and during restarts;

- 	transmission of RS and  CTM data as they are received in accordance with priorities.

m. 	Maintaining the survivability of the SHC (software-hardware complex) software during information exchange :

- 	synchronization of configuration data (Regulatory and reference information – RRI) of the working and backup sets;

- 	monitoring the status of communication channels with the formation of diagnostic information and the installation of appropriate quality attributes;

- redundancy of receiving communication channels with provision of automatic switching between the main and backup receiving channels.

- 	issuance of transmission/reception status signals for monitoring.

- 	implementation of measures to prevent the transmission of false information to correspondents during reconfiguration (switching on, restarting, switching to a backup set, damage and restoration of channels);

n. 	The following information processing functions shall be performed:

- 	transformation and unification of data formats depending on the exchange protocols via different channels;

- 	aperture filtration of CTM;

- 	inversion of individual (specified in the RRI ) RS.

o. 	Service functions:

- 	implementation of service functions using automated workplaces  (AWP ) of the remote control operators;

- 	AWP software of the remote control operator  must provide access to current SCADA data , as well as to RRI data;

- 	implementation of service functions - registration and archiving of vital service information, monitoring of  SHC operation, automatic and semi-automatic diagnostics, tools for the formation and maintenance of RRI.

p. 	Registration of service information:

- 	data on the state of communication channels, including statistics on failures; data on the results of automatic diagnostics of the SHC,

- 	about restarts and switching to reserve and working mode,

- 	data on the results of automatic diagnostics of the CP  received via channels,

- 	data on the actions of system administrators and automated workplace users.

q.	Monitoring:

- 	AWP software  of the remote control operator must ensure control of current values of the RS and CTM information. The main form of information output is tabular. The RS and RS and CTM information must be displayed using technological (symbolic) names;

- 	the status of each RS object must be displayed, indicating the time of the last change in status and quality attributes - malfunction, blocking, manual input;

- 	the output of the current value of each CTM must be provided indicating the quality attributes - malfunction, replacement with a reserve, going beyond the limits, blocking, manual input. The display of CTM values must be done in the format of physical (scaled) values.

r. 	Diagnostics of the communication channel status: diagnostic information must be displayed on the control format as a formatted text with the mandatory indication of the time of occurrence of the event in real time (event log):

- 	operations for generating diagnostic information must be performed continuously in real time during the process of receiving information;

- during the process, diagnostic information about reception errors (end of information reception, etc.) should be reflected with the possibility of later recording in a file,

- the capacity of monitoring the current status of all reception channels shall be ensured, including the indication of reception via the main and backup channels.

s. 	Configuration data management (Regulatory and reference information - RRI):

AWP software of the remote control operator contain tools for editing and monitoring RRI (Regulatory and reference information).

- 	RRI data must contain:

- for each channel: name; exchange protocol identifier and data specific to this protocol; identifiers and volumes of information (for each CP for multipoint channels); tables of addresses of information objects; the quantity  and numbers (addresses) of CP for multipoint channels; indicator of the presence and type of reserve;

- for each RS: source address; symbolic (technological) name; sign of inversion;

- for each CTM: source address; symbolic (technological) name; scale factor and offset of the scale start; technological limits; address of the source duplicating the CTM;

- 	RRI must be stored in the database.

t. 	Redundancy of the CR&TS system and its components:

- 	for reliability, hot standby of the central control system as a whole (two-machine complex) with software arbitration of the CR&TS system operation shall be used;

- 	additionally, forced manual switching of roles with corresponding signaling in the AWP of the remote control operator shall be provided.

# Requirements for the functions of the basic SCADA control system

The basic supervisory control and data acquisition  system shall include solutions for receiving, processing, visualizing, storing data on the operation of the power system in the area of responsibility of the grid enterprise, and information exchange  with adjacent control centers.

a.	Real-time database (RTDB). The real-time database shall contain the current values of the facilities' parameters. The current value includes: the parameter value, quality attributes, the time of information generation, the time of value receipt, etc.

b.	User interface. The user interface should be a multi-window human-machine interface designed in a single style for operating and configuring the system.

User interface key features shall include:

- the ability to display information on individual (including multiwindow automated worksplaces) and shared display devices;

- displaying information about the current or retrospective state of electrical equipment and the operating mode of the electrical network in the form of mnemonic diagrams, graphs, tables, diagrams, logs;

- quick transition from one presentation of information to another;

- displaying the status (state) of the displayed information;

- scaling of displayed information, changing its level of detail;

- sorting and filtering the displayed information according to various criteria;

- layered display of displayed information;

- selecting a section of the network and displaying it in a separate window;

- search for elements on diagrams of electrical network facility;

- availability of a built-in editor for mnemonic diagrams, logs, reports and other display screen forms;

- availability of a standard library of electrical and information network elements;

- in all cases, the interface details shall be agreed upon by the relevant specialists of the Company.

c.	Display of operational information

SCADA for data exchange  with the control of the facility shall ensure interaction with systems for acquisition and transmission of technological information and access to them through the human-machine interface.

SCADA shall be able to display the following types of operational information:

- 	the state of the switching equipment, analog values of TM, the AWS system in the diagram (in graphical format),

- unacknowledged signals by using additional graphic markings or backlighting,

- TM exit beyond the setpoints and allocation of the corresponding equipment.

- 	display of erroneous signal on the diagram using additional graphic marks or highlighting,

- TM graphs.

Display of operational information shall be possible using various types of display screen formats.

In addition to visualizing operational information on user screen formats, SCADA shall provide the following:

- display the log of recent events and alarms.

- display of telemetry graphs: graphs of current measurements on a given sliding interval, graphs of archived measurements acquired from the SCADA archive, external archive or via the OPC HDA protocol.

- sound notification when a remote signal is received.

- display of the presence of an unacknowledged event at an energy facility.

- highlighting on the diagram when  equipment is removed from remote control,

- acknowledgement of each RS  and the list of events as a whole,

- remote control,

- transfer of the signal to manual control and removal from manual control (set on telemechanical control).

- control of the Video Wall (large screen installed in the CDS),

- recording of RS, EWS  signals and displaying outputs beyond the setpoints in the database,

- manual maintenance of the status of non-telemechanized equipment.

- display of deviations from the norm on a diagram and in a tabular presentation.

d. Topology processor.

The graphic editor shall allow automatic construction of topological connections between elements based on the graphic representation of the diagram. Based on topological connections, an electrical model shall be constructed, electrical units and their current state - the presence of voltage – shall be determined. The diagram is presented as a set of interconnected elements of the main equipment.

e. Graphical editor.

SCADA shall include a graphical editor that provides broad capabilities for creating schematic solutions and is oriented towards the requirements of power engineers. In general SCADA shall provide a graphical representation of the main equipment, equipment of secondary switching systems of power facilities in the format of the following documents:

- 	single-line operational diagrams of main 110-35 kV electrical networks;

- 	single-line operational diagrams of 10-6/0.4 kV electricity distribution networks;

- 	DC electrical panel circuits - for own needs;

- 	data transmission system, information acquisition and transmission systems diagrams, Central Control Service diagram;

- 	diagrams of technological systems;

- 	line passport , structural diagrams of power transmission lines;

- 	area topographic plans (GIS);

- 	an arbitrary image using independently created additional elements.

The graphical editor shall have the following capacities when developing a circuit design:

- 	the ability to expand built-in libraries of equipment elements;

- 	the availability of a system of flexibly customizable element styles in conjunction with libraries that ensure the fulfillment of all customer requirements;

- 	libraries of various elements providing a compact representation of equipment as part of a connection and an electrical installation as a whole,

- initial creation of information model objects on a graphical diagram.

f.		Network management subsystem. Updating the diagrams.

The basic capacity of SCADA shall  be the efficient updating of network and energy facility diagrams.

The efficiency of updating the schemes/diagrams shall be achieved by the SCADA concept, in which the central role is given to the general network model. The visual representation of the model shall be a mnemonic diagram.

Such user actions in the system as switching, placing posters (special signs) on equipment, making records in the operational and technological logbooks shall be reflected in the operational network diagram. SCADA shall be successfully integrated with teleinformation acquisition and transmission systems, which shall be able to automatically update the diagram and to remotely control the equipment.

In the course of performing their responsibilities for maintaining operational and process logs, operational staff can simultaneously receive an up-to-date network diagram, accessible to other employees of the enterprise and software systems that require information on the current state. Additionally, when updating the operational diagram by the user, records in the logbooks shall be made automatically, in accordance with the system configuration.

The user shall be relieved from the need to duplicate the input of the same information, since it can be entered into the system once in various ways and shall be available in all forms of its presentation. The network management subsystem shall allow updating schemes of any level: electrical networks, district networks, city networks, power supply schemes of industrial enterprises, power systems, substations, electrical schemes of stations, relay protection and automation equipment, CDS devices.

g. 	Network Management Subsystem. Main Features

- 	display of the state of switching devices during switching operations both using the main equipment (switching devices) and on the secondary equipment diagrams (state of relay protection and automation), CB/PB automats.

- equipment status registration: phasing, position of the switching device, busbars, status of the switching device drive, installation/removal of operational interlocks.

- 	fixing the installation location of numbered portable protective grounding and shunts.

- 	placement of posters and marks that allow for a quick assessment of the current situation and ensure collective work of operational staff with the diagram.

- 	dynamic coloring of the main equipment, depending on the state (energized, de-energized, grounded).

- 	maintaining events statistics.

- 	printing out the schematic diagram status,

- 	search and selection of elements on the diagram according to a number of criteria.

h. Network control subsystem. Organizational and technological tasks to be performed.

Operations to change diagrams must be strictly regulated and limited by user rights. The execution of these operations must be implemented in the process of performing the following procedures:

- 	maintaining an operational diagram, maintaining an electronic logbooks by users authorized to perform work.

- 	recording the operational staff shift change of the facility, transfer of information on the shifts.

- 	use of a system for preparing, coordinating, authorizing and recording the execution of standard and one-time switching templates and switching programs.

i.  Network control subsystem. Information functions for working with the diagram.

- 	display of search results and equipment selection directly on the diagram.

- 	viewing data related to the equipment on the diagram (passport or design data, etc.) from the databases available to the Customer.

- 	automatic formation and illumination of normal (according to normal current sections) and current (at a certain point in time) feeders.

- 	hyperlink mechanism (including dynamic ones).

j.		Data acquisition and exchange.

The data acquisition and exchange system must ensure:

- 	reception (acquisition) of data from existing supervisory control systems;

- 	reception (acquisition) of data coming from ТМ and ACS TP;

- 	transmission of control actions (remote control commands) to the ACS TP & TMS SS TM;

- 	data exchange with adjacent control centers.

Data exchange methods:

- 	transfer of data by periodic polling of sources;

- 	transfer of data from the source as needed (when data changes).

The SHC must support data exchange via redundant communication channels.

The SHC must provide automatic monitoring of the operability of the redundant source and, if necessary, switching to the redundant source.

During operation, the SHC must perform diagnostics of data acquisition by using:

- 	sending a request to UTM, ACS TP and related control systems;

- 	control of the requested result;

- 	monitoring and displaying information sent and received from the UTM, ACS TP and related control systems;

- 	providing communication statistics

k. 	Data processing

The SHC shall perform processing of the following types of data:

- 	discrete data (status, positions);

- 	analog data (telemetry, manual input, calculations);

- 	integral values (meters, integral calculation);

- 	status information;

- 	events.

Data processing shall include two stages – preliminary (control of input data) and main.

Pre-processing of data shall include setting the system and astronomical time stamp, checking the fact and frequency of updating.

The main part of the processing should include conversion into engineering quantities, calculation of pre-calculation values, limit control, etc.

l. 	Data archiving

SCADA must provide:

- 	storage of data necessary for the functioning of the SHC;

- 	storage of data collected through information exchange channels;

- 	storage of processed data;

- 	storage of archives of logs, lists, reports.

The SHC shall implement the ability to create backup copies of system information to restore the system's operation after a failure.

m. 	Switching controls

SCADA must implement most technological procedures, allowing flexible adaptation to the regulatory and technical documentation effective at the enterprise, taking into account, among other things, the order and sequence of switching.

Switching by SCADA implies automation of routine operations, accompanied by increased efficiency and safety of performance, and shall ensure:

- 	planning the implementation of switches with determination of the date and persons responsible for performing the work.

- 	planning the composition of switching operations: technical switching measures, standard one-time switching forms necessary for recording the strict sequence of staff actions.

- 	a procedure for coordinating and recording the status of electronic documents on switching, which allows for the separation by time and staff of actions on developing electronic documents, conducting switching, and actions on updating the operational diagrams.

- admission of the staff to perform work (by radio tags).

- 	updating the network diagram when switching occurs.

Basic switching control capabilities must be provided, including:

- 	switching based on the selected type of electronic document or without it,

- 	checks by  using algorithms for software blocking incorrect user actions when compiling a list of operations;

- planning of switching operations on a current, retrospective or planned basis, taking into account already planned switching operations on adjacent electrical installations;

- 	output of a list of consumers associated with the shutdown of the selected electrical circuit;

- 	setting the state of the network diagram when performing a group of operations as a whole, or with a sequential division of individual operations by time;

- 	setting the required document approval procedure, without which it will not be possible to perform switching;

- 	advanced means of printing of the circuit status.

SCADA shall  have a built-in subsystem for analyzing the correct execution of switching operations supervising the following:

- 	switching on grounding knives under voltage;

- 	switching off disconnectors under load;

- 	activation of operational blocking;

- 	power outage for consumers.

The switching log must provide:

- 	quick access to information.

- 	saving information about switches to a file.

- 	the ability to print an operational task in the form of a standard switching template;

- 	preparation of one-time switching templates and work with them.

- 	preparation and storage of a database of standard switching templates.

- 	checking the possibility of executing a standard switching template in the current state of the power facility diagram,

- 	maintaining the status of the switching template (draft, in progress, completed, etc.).

- 	automatic generation of the reverse template,

- 	creation of one-time switching templates based on standard templates in electronic format and work on them.

- 	automatic recording of actions in the operational network diagram based on the template.

In addition to the above, when switching, the system shall prompt the sequence of switching.

n.	Managing tasks on the network

SCADA shall  enable automation of processes for managing planned and emergency recovery work in the network, in which users from among administrative and technical staff may also participate.

To record network managing tasks, SCADA must include the following accounting tools:

- 	accounting of work assignments, prompt registration of the status of work performance, tracking the status of work according to assignments and instructions.

- 	accounting of operational staff, transport and other enterprise resources during planning and execution of tasks.

- 	recording information about events that have occurred related to technological failures in the network, including information about failures investigation reports,

- 	recording the results of inspection of the main equipment and secondary switching systems and associated defects or damage.

In addition to the tasks of recording and monitoring the current situation, as well as generating reports based on the registered information, the network control subsystem must provide additional capacities for planning and performing tasks on the network:

- 	development and approval of applications for the performance of works related to the commissioning/decommissioning of main equipment;

- 	planning of network operating modes for the selected period, development of repair schemes taking into account the current and planned composition of switching;

- 	development of a plan for windows between repairs and renovations, taking into account the planned work on both sides, ensuring the network's virtual topology, as well as its operating modes.

o.	Electronic logbook subsystem.

SCADA shall have the capacity to create multiple Operational and Technological logbooks that provide tasks for operational and technological management of the networks.

Entries in logbooks can be made manually, based on the actions of operators at various levels of the network enterprise, as well as related organizations that have access to the project.

Access rights to logbook entries must be defined by the project settings. Logbooks entries must be stored in the SCADA DB and contain information about the parameters and time of the event at the power facility, an explanatory part, and data about the person making such entry. Logbooks must be fully integrated with each other and with the electrical network model, so that the transition between logbook entries must be ensured in the presence of a logical relationship, as well as from a log entry to a circuit element and back.

It shall also be possible to run logbooks without a diagram/scheme.

SCADA must ensure operation with the following list of operational and technological logbooks:

- 	operational log;

- 	event log;

- 	log of deviations from the normal scheme;

- 	log of operations with SS FSS and SP;

- 	poster operation log;

- 	of RP&A and ARA indication log;

- 	log of changes in consumers' power supply sources;

- 	journal of assignments and instructions;

- 	a log / template of switching, which is compiled automatically during the switching of the circuit;

- 	log of technological failures (VT TF);

- log of consumer applications (market suppliers);

- 	equipment defect log,

- a log of requests for equipment to be taken out for repair.

Power Supply Change Logbook

The power supply change logbook shall allow for keeping track of changes in power supply to consumers. Moreover, there shall be the capacity  to link each facility with the “ENA” CJSC subscriber database to display the exact number of de-energized/switched subscribers.

Technological failures logbook

The logbook recording technological failures shall provide all necessary capacities for recording information on interruptions in the transmission of electrical energy.

Thelogbook shall create reporting forms for any period of time with the calculation of all final indicators.

The following indicators shall be recorded in the technological failures  logbook:

- 	data on the fact of the event (sector of the network company, date, type of failure, etc.).

- 	data on the scale of the event (list of consumers, disconnected supply points, their characteristics: category, power, voltage class).

- 	findings of the investigation of a technological failure.

- 	results of restoration work (organizational and technical reasons, date of reconnection - including partial).

- 	additional user parameters. The data of the report on de-energized subscribers shall be generated automatically based on pre-prepared subscriber directories and analysis of the current network.

Log and module of consumer complaints about power outages

To register consumer complaints, SCADA shall have a module that allows recording information about a complete or partial loss of power supply using corporate information systems created at the Enterprises (for example, from the Call Center). The module shall provide information about power outages based on consumer calls received by the Call Center and display the caller's connection point on the dispatcher's screen  indicating the possible point/location of the event. The module should also perform the reverse function - via feedback through the dispatcher or the RDMT, inform the Call center or the Consumer Service Center about a planned or emergency power outage. Moreover, in case of numerous calls, one signal should be generated, which will be sent to the Central Control Service; when viewing the signal data, the number of calls and all the necessary information about the outage shall be displayed.

Appropriate logbooks shall be generated for the above described alarms.

Log of equipment defects and malfunctions and the progress of their elimination

It is necessary to have a module for recording equipment defects and malfunctions, integrated with the electrical circuit/diagram. Automatic transition from the record to the circuit element and back must be provided.

The module must provide the capacity to select records by:

- 	the planned date for eliminating the defect (indicating a specific date or period);

- 	the unit responsible for eliminating the defect;

- 	all unresolved defects;

- 	defects for which the deadline for elimination has expired.

The module shall allow for the postponement of the defect elimination deadlines.

Main features of the electronic Logbooks subsystem

SCADA shall provide the following capacities when working with logs:

- 	manual addition of a new entry from the network diagram;

- 	manual addition of a new entry in the log window interface;

- 	editing records, saving the history and authors of changes;

- 	printingout of the logs.

The following types of entries into the logbook shall be provided:

- 	actions at the facilities  – recording switching, operational current setting/blocking, protections setting/disconnection, etc.

- 	acknowledgement of remote signals and messages about exceeding the installed values;

- 	verification actions, results of site visits and inspections;

- 	negotiations between operational staff, recording of instructions;

- 	placement and registration of mobile and repair teams at destinations;

- 	installation/removal of mobile elements – portable grounding, poster, etc.

- 	marking accident locations.

p.	WebGIS or GIS Module

The WebGIS module shall allow the creation of a geo-passport for the area of interest, displaying within it ortho- and photo-bases with the application of the geographic location of electrical network facilities, including data from equipment and power transmission line passports, feeder tablets, etc.

Eventually, SCADA shall integrate data from a geographic information system, electrical network diagrams for all voltage classes.

The WebSGIS module shall be designed to work with large volumes of geodata as a means of viewing prepared geoinformation, as well as for managing spatially distributed resources of an electrical network Company.

For GIS functionality of it is necessary to:

- 	perform import into the geodata format scheme or implement a configuration that ensures loading "on the fly" of geodata from pre-prepared raster or vector maps of the network Company's service area. As a rule, the sources are corporate GIS or Internet geoservices.

Under these terms of reference inclusion (import) of data available at “ENA” CJSC in ArcGIS format must be ensured.

# Detailed requirements for SCADA architecture:

SCADA shall have:

- modular architecture with a set of optional functional modules and drivers;

- built-in mode for configuring and editing modules and drivers – a separate processing and editing media should not be used;

- the ability to process an unlimited number of input/output signals with performance dependent only on the hardware and communication channels;

- the ability to be used  by an unlimited number of clients and users;

- local and remote access to data from any device via a web browser;

- storing retrospective data in database PostgreSQL, MS SQL Server ;

- installation on 64-bit versions of Windows 10 Pro / Enterprise, Windows Server 2012 and above, Linux ( Alpine , Ubuntu , Arch Linux , Fedora );

- support Google Webb browsers Chrome , Firefox Mozilla , Microsoft Edge ;

- supported data exchange protocols – IEC 60870-5-101/103/104, IEC 61850, Modbus RTU , Modbus TCP , OPC DA , OPC UA , proprietary protocols of metering devices used by “ENA” CJSC

- the ability to integrate with third-party applications via API in JSON format .

The SCADA software of the ODC level of “ENA” CJSC must be interfaced with the EMS, DMS, OMS modules, which provide automation of control based on the mathematical model of the Enterprise’s network complex.

EMS / DMS module shall provide solutions to the following tasks:

- analysis of established modes of network operation;

- assessment of the state of the electrical network;

- calculation of short-circuit currents;

- short term and long term energy consumption forecast.

The OMS module shall provide solutions to the following tasks:

- control of switching during the emergency response process;

- automatic notification of consumers (via personal accounts, SMS

notification) of power outage;

- transfer of switching template to the automated workplaces of mobile teams;

- display of data on the current locations of mobile teams;

- generation of a report on disconnection of consumers and de-energization of equipment.

# Requirements for TM Boxes

New TM Boxes must be installed at facilities of the following Types:

- Type 1.1;

- Type 1.2;

- Type 1.3;

- Type 2.1;

- Type 2.2;

- Type 2.3;

- Type 4.2.

Type 4.1 facilities are not equipped with additional equipment of the ACS TP (TM), since the existing SM-160-02M type ESMS controller are used.

For the facilities of type 3.2.1, 3.2.2, 3.3 the TM Box shall be  installed if the Contractor does not provide for the installation of controllers and related equipment in the existing Boxes and cells in the facilities of “ENA” CJSC  (all of the following also applies to the equipment installed by the Contractor as replacement of the Box inside the equipment of “ENA” CJSC).

TM Boxes are intended for:

- collection of discrete signals of the position of switching devices, control keys; emergency and warning signaling of relay protection and automation systems (RP&A);

- collecting analog signals from electricity meters and telemetry sensors;

- remote control of switching devices through relay protection and automation (RP&A) terminals from higher control levels;

- sharing obtained data with higher control levels;

- remote configuration, status monitoring and diagnostics of Box equipment.

General requirements for the TM Box:

- the TM Box must be supplied as a complete set (factory-made);

- design documentation for the Box, including electrical circuits/diagram  must be developed by the equipment manufacturer in compliance with all regulations;

- the Box operating mode is continuous.

Requirements for the TM Box design

The TM Box shall be made of stainless steel or galvanized metal, or coated with weather-poof paint, with at least 3-year warranty, or must be made of fireproof plastic, have the possibility of one-sided maintenance through the front door, and shall include:

- Box body with fasteners and a mounting panel for installing equipment;

- a set of design-configurable equipment;

- terminals for connecting internal and external wiring;

- cable clamps for input and fixing of external wiring:

- grounding clamp on the grounding busbar at the bottom of the Box.

The Box shall be cooled by natural convection and thermal radiation.

Conductors (or cables) for internal connections of the TM Box must be secured or laid in tubes or wiring ducts.

The Box door must be equipped with locks to protect against unauthorized access and have a door opening sensor connected to the remote alarm system.

The thermal effect of the rated current of all electrical circuits of the Box must not result in the Box temperature exceeding the ambient temperature by more than 10°C.

Overall dimensions, maximum weight are determined by the Box's purpose and the installed equipment. The Box's protection rating must be at least IP 54.

Power requirements for the TM Box:

The TM Box must have at least two single phase  inputs from AC power sources of 220 V 50 Hz. Input of backup power in case of power failure at the main input must be activated automatically by ARA.

ATS must be designed on the basis of an electronic phase switch with automatic selection of the operating power supply phase.

The Box equipment must ensure operation in normal and emergency mode (complete loss of power at the main and backup inputs). Switching from normal to emergency mode must be triggered automatically.

Power backup in emergency mode must be provided by a supercapacitor-based UPS having a service life of at least 10 years, a range of operating temperatures from -40 to +65 CO and ensuring the operation of the Box's active equipment (TM controller and transmitting device/modem) sufficient to transmit signals of the object's last state until the voltage on it disappears, but not less than 2 minutes. Switching power to UPS must be performed automatically. At non-reconstructed (non-modernized) facilities, it is allowed to use rechargeable batteries of a different type only in case of a requirement to transfer minimum volume of data, however, in this case, temperature of at least +5°C shall be maintained in the ТМ/RS Box to maintain battery capacity and not reduce battery life.

“ENA” CJSC  reserves the right to use other types of UPS.

In order to increase the reliability of the power supply circuit, the active equipment of the Box must be powered from a  ~220 V source without the use of external power supplies.

The ТМ Box shall be equipped with a 220 V AC service socket at 50 Hz frequency for connecting electrical appliances with a power of at least 200W.

Requirements for the ТМ Box mounting kit:

- modular circuit breakers must be used to protect AC and DC power circuits.

- technological connections of the Box devices must be made using single-core or multi-core copper wire with a cross-section of 1 mm².

- when using multi-core wire, it is necessary to use pin-type sleeve terminals.

- wiring of power supply circuits for Box devices from the power supply unit must be made  through intermediate terminals.

- interface connections of the Box devices must be arranged using a specialized RS -485 or Ethernet cable .

- wires and cables connecting Box devices must be laid in wiring ducts so that interface connections and cables are separated from power connections and cables.

- mounting of modular devices and intermediate terminals must be arranged on a DIN rail.

- all interfaces in the ТМ Box must be protected from voltage surges (e.g. due to an accident or lightning strike), electrostatic effects, etc., by means of appropriate equipment- interface protection devices - in accordance with the requirements of IEC 61312-1.

# Requirements for the programmable controller

The main device at the facility level automation shall be the multifunctional controller that ensures the acquisition of  information from the RS, TM  from modules RS, TM, the transmission of RC commands to the relay protection and automation terminals, and communication with higher levels of the system.

The controller may have a modular design and ensure all the requirements listed below by assembling the corresponding modules. Moreover, if the Contractor does not provide for installation of a new ТМ Box, then all the above requirements for the UPS must be ensured by the corresponding module(s), which also applies to the automatic ARA between the phases of the facility for uninterruptible power supply to the controller.

Controller requirements:

- data exchange with a higher control/management level using IEC 60870-5-101/104, IEC-61850 protocols (upon request);

- data exchange with slave devices (RS, TM modules, RP&A terminals, measuring transducers, meters) using protocols IEC 60870-5-101/103/104, IEC-61850, Modbus RTU, Modbus TCP, Spa-BUS;

- time synchronization from own GPS/GLONASS antenna with internal clock accuracy of no worse than 1 ms;

- availability of ports (not less than):

- 2 x Ethernet 10/100 Mbps​ for direct connection to optical communication channels;

- 1 x USB Host (USB-A);

- At least 2 x RS-485 with the possibility of expanding the number of ports;

- 3 × discrete/analog input/output "open collector";

- 1 × discrete input/output "open collector";

- GSM/GPRS/3G/LTE modem;

2 x SIM (one SIM card in the network at a time );

- supply voltage  220VAC with the possibility of having backup power supply;

- operating temperature range -40 to +65 °C;

- to have an industrial design and meet the requirements for electromagnetic compatibility for placement at electrical substations in close proximity to electrical installations confirmed by certificates;

- withstand power interruptions of up to 1 s without rebooting, for example, when operating an ARA;

- the ability to create user algorithms (user logic, additional calculations) using FBD (IEC 61131);

- the accuracy of time matching to events is no worse than 1 ms;

- the controller housing must provide protection from humidity and dust (minimum protection level IP 20);

- the design of the controller housing must restrict access to the information carrier;

- the controller must be designed for placement in limited spaces in specialized Boxes and racks with mounting on a mounting panel;

- the controller must be cooled by natural convection.

The controller must be maximally protected from possible interference, placed in a separate case, have special protection against complete power failure, which correctly terminates the operation of the main processor, guarantees the integrity of the information stored in it, and ensures the safety of archives and settings for a long time.

The controller must allow complex processing of information. The software used by the controller must allow flexible configuration of the controller data processing according to the user's algorithms using built-in technological programming languages.

The controller must include a software key for selecting a remote control location (control capture) to ensure the possibility of remote control from one operator location.

The controller must be able to collect oscillograms from digital relay protection terminals and transmit them to dispatch centers.

In addition to the functionality of collecting operational teleinformation, the controller must perform the functionality of the Data Acquisition and Transmission  Unit  of technical/commercial metering and poll the meters installed at the inputs to the 0.4 kV switchgear.

The controller's performance must be at least 2000 signals.

The controller must, if necessary, collect non-electrical parameters (air temperature, humidity, door opening signals, etc.) entered via unified analog inputs 4-20 mA.

The controller must have its own diagnostic tools with generation of diagnostic result signals in the controller signal base. Diagnostic result signals can be transmitted to the upper control level and also used for local signaling.

Diagnostics of controllers must be performed automatically both upon switching on and continuously during operation.

The controller must be equipped with automatic time synchronization and determination of the installation location coordinates (indicating latitude and longitude).

The source and parameters of time synchronization and coordinate determination must be configured in the controller and executed:

- 	from an external receiver of signals from global navigation satellite systems of precise time (GLONASS/GPS) using standard protocols (NTP, SNTP);

- 	via the built-in GPS/GLONASS satellite synchronization module.

It should also be possible to configure time synchronization from the upper level using the IEC 60870-5-104 information exchange protocol.

The controller shall able to operate both in local mode and in the mode of exchanging information with upper control levels. When operating in local mode, the controller must collect and archive information in non-volatile memory for at least 100 events. When operating in the data exchange mode, the transfer of the latter must be carried out upon request from upper control levels.

The controller must perform automatic diagnostics of the state of communication channels with lower-level devices of the SHC and issue warning messages when communication is lost. The controller must support the SNMP protocol at the upper level to ensure monitoring of network devices. The controller must perform automatic diagnostics of the status of:

- channels (including loss of voltage at the inputs);

- hardware status;

- communication channels to higher levels of management.

Controller software requirements:

The software installed on the controller must include basic software based on the Linux real time operating system and system software (SS) –  executive system.

The System Software shallt provide all functions implemented directly in the controller - polling of lower-level devices (metering devices, MFMT, input-output devices, MP terminals of the relay protection and automation systems, and other devices), processing, storing archive data, and transmitting information to the upper level. The System Software  must also provide operation via the WEB interface. The WEB interface is designed to monitor the operation of the controller and the main set of configuration functions. The WEB interface is available when connected to the controller via an Ethernet communication channel, or via a static address via a GPRS connection. The WEB interface, as well as the controller System Software  must be supplied with all controllers installed and ready for operation.

To work with the software installed on the controller, the software of the development environment installed on the external computer of the engineer's workplace must be used:

- controller polling utility. The polling utility must be included in the distribution kit of the development environment program. It must be able to poll the controller via various communication channels, save the polling results, adjust the parameters and synchronize the configuration of the polled lower-level devices. The utility must also support direct polling of lower-level devices via various communication channels. Polling by the utility must be performed via the controller and its communication interfaces. The polling utility must allow saving the results of monitoring controller's operation, polling the controller by IP address, as well as via GSM connection (CSD polling mode). One of the main purposes of the polling utility is to carry out facility starting up and adjustment works, initially check the communication channel, generate a report on the facility, and demonstrate data transfer to the upper level;

- controller configuration system shall be included in the distribution of the development environment program and used to configure the controller;

- optionally, there shall be the possibility of supplying a system for encrypting transmitted data. The client part of this system in the form of a software module shall be integrated into the controller software. The encryption system shall be supplied optionally if ordered for  protected communication channels.

The controller software must allow for configuration, testing, and diagnostics of the controller operation.

The software and hardware of the controller must include software and hardware protection against looping - a “watchdog timer”, with the help of which a reboot should be performed in the event of software failures or a reboot of the GSM module in the event of loss of connection to the network, protection against attacks of the "denial of access" type (DDoS), the ability to replace factory passwords with user passwords in accordance with the “ENA” CJSC requirements for the security policy.

# Requirements for modules RS, RC, TM

Where the Contractor provides for the installation of RS, RC and TM modules, the following requirements shall apply:

- to have an industrial design and meet the requirements for electromagnetic compatibility for placement at electrical substations in close proximity to electrical installations confirmed by certificates;

- the number of inputs based on the requirements of the facility;

- the presence of galvanic isolation from internal circuits of at least 2500 V;

- Possibility of installing modules: "dry contact" / presence of voltage;

- generation of a two-position signal "on"/"off" on the module;

- interface: RS -485 Modbus RTU or Ethernet, or be a built-in controller module;

- the presence of a buffer for storing information in the event of a connection failure;

- - device level timestamping;

- the accuracy of time matching to events is no worse than 1 ms;

Requirements for TM modules:

- to have an industrial design and meet the requirements for electromagnetic compatibility for placement at electrical substations in close proximity to electrical installations confirmed by certificates;

- one three-phase or three single-phase measurement channels;

- measurement of instantaneous parameters: voltage, current, power;

- storage of accumulated energy values;

- individual values for all 3 phases and total for the three-phase load;

- measurement of active, reactive and apparent power and energy;

- measurement of power factor and phase angles;

- measurement of peak values of currents and voltages;

- presence of a function for detecting incorrect phasing;

- rated current - 5 A

- accuracy class 0.5S ;

- interface: RS -485 Modbus RTU or Ethernet, or be a built-in controller module,

- the presence of a buffer for storing information in the event of a connection failure;

- device level timestamping;

- the accuracy of time matching to events is no worse than 1 ms;

Requirements for installation of RS, RC, TM modules

RS and RC modules can be installed both in relay protection compartments, and in TM and ACS  TP Boxes (is part of the controller), while all ТM modules shall be installed in the relay protection compartments of the high-voltage cells.

Requirements for installation inside the RP cells:

- modules shall be mounted on a DIN rail from the reserve or mounted additionally;

- the power supply circuits of the modules are mounted using FRLSLTx  3x1.5 cable, laid in the cable channels of the switchgear cells through intermediate terminal assemblies. Terminal assemblies are used from the reserve or mounted additionally;

- connection of signals to the RS modules is executed by a single-core wire with a cross-section of 1 mm² from terminal assemblies to which signals of the position of switching devices, control keys, and relay protection and automation signals are output. The wire is laid in mounting cable-ducts;

- RS -485 interface trunk lines are laid with a specialized cable with a bus assembly on interface splitters or intermediate terminal assemblies, while the ends of the cable are crimped with sleeve pin tips. In a standard solution, a bus of RS modules, a bus of TM sensors and a bus of RP&A controllers are laid to the Box. Bus cables are laid in cable duct of switchgear cells. In case of external installation, RS -485 interface trunk lines must be laid with appropriate external influences protection cables.

# Requirements for communication channels

The following requirements shall apply to communication channels:

- intra-system communication of automation facility level devices must be executed via RS -485 interface at a speed of 9.6…115.2 kbit/sec or Ethernet;

- communication between the automation facility and the upper level must be executed via cellular communication channels of the 3 G /4 G standard (reserve channel) and Ethernet(main channel).. The availability of the latter shall be a priority. Providing an Ethernet output is mandatory for any solutions.

Communication between first-level facilities s and the servers of JSC “ESA” shall be performed by “ENA” CJSC.

# Reliability Requirements

The following reliability requirements shall apply to the system elements:

- mean time between failures – not less than 125,000 hours;

- average service life – 20 years ;

- average recovery time (excluding spare parts delivery time) – 1 hour.

# Information Security Requirements

Ensuring the security of protected energy facilities of Electric Networks of Armenia CJSC must be achieved through the application of a set of organizational and technical measures to protect information aimed at blocking (neutralizing) threats to information security, the implementation of which may lead to a violation of the normal operating mode and the controlled (supervised) facility.

As part of the work, it is necessary to design and implement a set of organizational and software and technical measures to ensure the information security of protected energy facilities (hereinafter referred to as the Information Security System (ISS= СОИБ)) taking into account the requirements of current legislation regarding the security of critical infrastructure facilities, as well as the requirements of the current regulatory documentation of Electric Networks of Armenia CJSC and this ToR.

Develop solutions to ensure information security, including:

- description of the protected object;

- analysis of information security threats and description of the potential intruder model;;

- current requirements for ensuring information security, clarified taking into account the provisions of the Company's regulatory documents, as well as the results of the analysis of possible threats to information security and the consequences that may arise as a result of the these threats;

- solutions for ensuring information security, including solutions for access control, registration and accounting, ensuring the integrity of information security software, anti-virus protection of information resources, ensuring network security, and managing information security tools;

- a structural diagram of a complex of technical means, superimposed on the corresponding diagrams of the information technology infrastructure of the facility, communication systems, etc. The diagram should highlight the technical means of processing, storing, transmitting and protecting information that are installed or modified within the framework of the project;

- a diagram of the functional structure.

When constructing the ISS, the existing information security tools (hereinafter referred to as ISTs) and software and hardware in Electric Networks of Armenia CJSC must be taken into account.

When designing and implementing ISTs, it is necessary to take into account the activities carried out within the framework of related projects in terms of information security.

When selecting technical tools, it is necessary to take into account the existing infrastructure of the facilities of Electric Networks of Armenia CJSC and the existing engineering support systems. The technical means of the ISS must have the necessary performance and interfaces for connection to the existing infrastructure of the facilities of Electric Networks of Armenia CJSC.

The composition, performance and configuration of the technical means of the ISS shall be determined at the design phase taking into account the results of collected baseline data.

The possibility of implementing individual security measures at the ACS TP (TM) facilities and other information infrastructure facilities subject to protection shall be determined at the design phase based on the results of collected baseline data. If it is impossible to implement individual security measures and (or) it is impossible to apply them to individual facilities and access subjects, including due to their negative impact on the functioning of the ACS TP (TM), respective measures shall be developed and implemented to block (neutralize) threats to information security:

• a list of information infrastructure objects (hereinafter referred to as IIOs) operating in the technological segment of the information infrastructure;

• impact objects – elements (resources) of IIOs included in the IIOs and placed at various levels of the technological segment of the information infrastructure;

• types of information processed by impact objects.

The set of implemented measures envisaged during the design of the ISS shall not have a negative impact on the normal operation mode of the ACS TP (TM).

Design solutions must provide for the construction of the following subsystems:

• access control subsystem;

• registration and accounting subsystem;

• subsystem for ensuring the software protection systems IST integrity;

• subsystem for anti-virus protection of information resources;

• subsystem for ensuring network security;

• subsystem for managing of the ISTs.

The preliminary composition of technical means of information security implemented at facilities in the general case, shall include: :

• Means of ensuring network security;

• Means of anti-virus protection for software of workstations and servers;

• Means of backup and recovery of information for workstations and servers.

The full composition and quantity of the supplied ISS equipment shall be determined at the design phase.

The supplied equipment must be supplied assembled and installed in telecommunication Boxes.

All supplied equipment must be serial and included in standard configurations.

The subscription periods for receiving updates required for the operation of equipment or software must be at least 24 months from the date of acceptance of the equipment or software by Electric Networks of Armenia CJSC.

All equipment must be new, not preowned. The equipment shall be  equipped with all the necessary cables/wiring to ensure its joint operation and connection to the power supply network.

All equipment offered for delivery must have  manufacturer's warranty of at least 36 months from the date of commissioning.

    - Requirements for network security tools

Requirements for the protection of communication channels installed on industrial controllers in switching points (SPs) 6-10 kV and transformer substations (TSS) 6-10 kV.

In order to ensure the integrity of information and in the presence of current threats during transmission via external communication channels, it is necessary to ensure the implementation of encryption at the level of controller and (or) network equipment of AP 6-10 kV and TSS 6-10 kV using IPsec technology.

Specific decisions on the composition and configuration of mechanisms and means for ensuring network security shall be determined at the design phase.

Requirements for communication channel protection equipment installed at 35 - 110 kV substations

The network security equipment must  perform the following functions:

• controlling (filtering, routing, connection control, unidirectional transmission and other methods of control) of information flows between devices, segments of the ACS TP (TM), as well as between information systems;

• management of interaction with external information systems.

• filtering at the network level for each network packet independently (the decision on filtering is made on the basis of the network addresses of the sender and recipient or on the basis of other equivalent attributes);

• restriction of passage of any traffic except the minimum required for the operation of the ISS.

In order to ensure the integrity of information and in the presence of current threats during transmission via external communication channels, it is necessary to ensure the implementation of encryption at the level of controller and (or) network equipment installed at the 35 110 kV substation, using IPsec technology.

Specific decisions on the composition and configuration of mechanisms and means for ensuring network security shall be determined at the design phase.

Requirements for means of protecting communication channels installed in the operational dispatch control of "ENA" CJSC.

The means of ensuring network security must implement the following functions:

- controlling (filtering, routing, connection control, unidirectional transmission and other methods of control) of information flows between devices, segments of the ACS TP (TM), as well as between information systems;;

- management of interaction with external information systems.

- filtering at the network level for each network packet independently (the decision on filtering is made on the basis of the network addresses of the sender and recipient or on the basis of other equivalent attributes);

- restriction of passage of any traffic except the minimum required for the operation of the ISS.

In order to ensure the integrity of information and in the presence of current threats during transmission via external communication channels, it is necessary to ensure the implementation of encryption at the level of controller and (or) network equipment installed at the level of operational dispatch control "ENA" CJSC using IPsec technology.

Specific decisions on the composition and configuration of mechanisms and means for ensuring network security shall be determined at the design phase.

Requirements for the means of protecting communication channels installed in the operational dispatch services of branches and operational dispatch control points of "ENA" CJSC

The network security means/tools must perform  the following functions:

- controlling (filtering, routing, connection control, unidirectional transmission and other methods of control) of information flows between devices, segments of the ACS TP (TM), as well as between information systems;;

- management of interaction with external information systems.

- filtering at the network level for each network packet independently (the decision on filtering is made on the basis of the network addresses of the sender and recipient or on the basis of other equivalent attributes);

- restriction of passage of any traffic except the minimum required for the operation of the ISS.

In order to ensure the integrity of information and in the presence of current threats during transmission via external communication channels, it is necessary to ensure the implementation of encryption at the level of controller and (or) network equipment installed at the level of operational dispatch control "ENA" CJSC using IPsec technology

Specific decisions on the composition and configuration of mechanisms and means for ensuring network security shall be determined at the design phase.

2.8.2 Requirements for antivirus protection tools (endpoint protection subsystem)

Anti-virus protection tools (anti-virus protection subsystem for information resources) shall perform the following functions:

- continuous protection of endpoints from malware infection;

- periodic checking of endpoints for malware;

- control over the connection of external devices (USB drives, CD drives, MTP mobile devices, modems);

- management of operating system firewall settings;

- protection against file encryption on shared network resources;

- control over changes to arbitrary files on disk;

- analysis of operating system logs;

- protection against exploits;

- centralized management and distribution of antivirus database updates;

- registration of incidents.

2.8.3 Requirements for information backup and recovery tools

Backup and recovery tools must ensure the capturing and storage of images of operating systems of server equipment and automated workstations in automatic or manual mode..

Hardware requirements for backup and recovery tools shall be  determined after collecting the baseline data.

# COMPOSITION AND CONTENT OF WORKS ON CREATING THE AUTOMATED SYSTEM

List of stages of creation of ACS TP & TMS:

- Discussion of the details of the implementation of the ToR,

- Development of design documentation (for 35-110kV SS, Data Center of Unified Dispatch Control (UDC) and  United Dispatch Service (UDS) of «ENA» CJSC individual sets of design documentation shall be developed. For 6-10 kV facilities, standard designs shall be developed, while the Contractor shall conduct a survey of all 6-10 kV facilities).

- Complete system with supplied software and hardware,

- Construction and installation works ,

- Commissioning works,

- Conducting preliminary tests ,

- Conducting trial operation ,

- Conducting acceptance tests ,

- Carrying out work in accordance with warranty obligations,

- Post-warranty service (to be discussed separately).

# PROCEDURE FOR DEVELOPING THE AUTOMATED SYSTEM

# List of documents and baseline data for the development

For the development of the ACS TP & TMS, the initial documentation on automation facilities is listed below:

- single-line diagram;

- secondary circuit diagrams (if any);

- type of relay protection and automation terminals used;

- list of required signals RS, TM, RC

In the absence of the specified documentation, a survey of the automation facilities shall be carried out on site.

# List of documents to be submitted upon completion of work

Based on the results of acceptance tests, a bilaterally signed test report shall be drawn up.

# Warranty Requirements

The manufacturer must guarantee the conformity of the supplied product with the technical documentation, provided that the consumer observes the operating and maintenance standards during the established warranty period. The warranty obligation consists of free repair or replacement of any defective component included in the product. The minimum warranty period is 36 months from the date of commissioning

# PROCEDURE FOR CONTROL AND ACCEPTANCE OF THE AUTOMATED SYSTEM

# Preliminary testing

Upon completion of the commissioning phase the preliminary tests shall be carried out including autonomous and comprehensive tests.

Autonomous tests within the automation facility are carried out by the Commissioning Contractor.

During comprehensive testing, the interaction of all levels of the system is checked. Comprehensive testing is carried out by a commission, including representatives of “ENA” CJSC  and the Contractor. Based on the results of preliminary comprehensive testing, a test report is drawn up, containing information on the completeness, operability and compliance with the requirements of the technical specification. If the commission's conclusion is positive, an Acceptance Certificate for Trial Operation is drawn up.

# Trial operation

At the phase of trial operation, “ENA” CJSC  shall analyze the results of system operation, draw up a trial operation log, which contains information on failures, malfunctions, faults, changes in the required parameters of the automation facility.  The Customer shall eliminate the faults of the system components and, if necessary, adjusts the settings of the software.

The trial operation period is 1 month.

Upon completion of the trial operation, a Certificate of Completion of Trial Operation shall be drawn up and, if the conclusion is positive, acceptance tests shall be carried out.

# Acceptance tests

During acceptance tests, the interaction of all levels of the system, completeness, operability and compliance with the requirements of the technical specification shall be checked. Based on the results of the acceptance tests, a commission consisting of representatives of “ENA” CJSC  and the Contractor shall draw up a test protocol and an Acceptance Statement  of the system into permanent operation.

# REQUIREMENTS FOR THE COMPOSITION AND CONTENT OF WORKS TO PREPARE AN AUTOMATION FACILITY FOR COMMISSIONING THE AUTOMATED SYSTEM

In preparation for the commissioning of the ACS TP & TMS “ENA” CJSC, with the assistance of the Contractor, personnel shall be trained in the operating documentation for the system.

# DOCUMENTATION REQUIREMENTS

All design documentation must be prepared in the form of typical  technical solutions, except for 35-110kV SS, Data Center of Unified Dispatch Control (UDC) and  United Dispatch Service (UDS) of «ENA» CJSC

Minimum composition of design documentation:

- an explanatory note containing a table of signals RS, TM, RC;

- single-line diagram;

- structural diagram;

- external wiring diagram;

- external wiring connection diagram;

- equipment and wiring layout plan;

- cable list;

- equipment specification.

# REFERENCE SOURCES FOR DEVELOPMENT

GOST 34.602–2020 “Technical specifications for the creation of an automated system”

GOST R 59793–2021 “Set of standards for automated systems. Automated systems. phases of creation”

GOST R 59792–2021 “Set of standards for automated systems. Types of tests for automated systems”

# ANNEX 1. Facilities connected to SCADA system of CJSC «ENA»

| № | Name |  | total quantity | Degree of automation |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | RC (full) | RC* (with limitations) | RS** (controller) | Data acquisition from ESMS | Notes |
| 1 | Total 110 kV substation, incl. |  | 28 | 24 | 2 | 2 | 0 |  |
| 1.1 | Substations with operating ACS TP |  | 17 | 17 |  |  |  | Data Acquisitions from operating ACS TP |
| 1.2 | Substations without ACS TP, with RP&A MPT |  | 7 | 7 |  |  |  | New ACS TP is under creation |
| 1.3 | Substations without ACS TP, with EM RP&A |  | 2 |  | 2 |  |  | New ACS TP is under creation |
| 1.4 | Subscriber SS |  | 2 |  |  | 2 |  | Results of telemechanization of CJSC "ESA". The contractor ensures the reception of data in SCADA CDS of the management and branches.. |
| 2 | Total 35 kV substation, incl. |  | 18 | 14 | 4 | 0 | 0 |  |
| 2.1 | Substations with operating ACS TP |  | 0 |  |  |  |  | n/a |
| 2.2 | Substations without ACS TP, with RP&A MPT |  | 14 | 14 |  |  |  | New ACS TP is under creation |
| 2.3 | Substations without ACS TP , with EM RP&A |  | 4 |  | 4 |  |  | New ACS TP is under creation |
| 3 | Total SPs, inc. |  | 173 | 133 | 40 | 0 | 0 |  |
| 3.1 | SP with operating ACS TP |  | 0 |  |  |  |  | n/a |
| 3.2.1 | SP without ACS TP, with RP&A MPT of «Lytik» type |  | 30 | 30 |  |  |  | It is necessary to organize voltage measurement on the 6(10) kV side and make the necessary additional calculations in SCADA |
| 3.2.2 | SP without ACS TP, with RP&A MPT of «ТОР-200»/ «ТОР-150» type | Reconstructed before 2025 | 62 | 62 |  |  |  | New ACS TP is under creation |
|  |  | To be reconstructed in 2025 | 41 | 41 |  |  |  | Automation of said SPs shall be implemented upon completion of reconstruction |
| 3.3 | SP without ACS TP, with EM RP&A |  | 40 |  | 40 |  |  | Non-reconstructed SPs |
| 4 | Total TSS facilities inc. |  | 2500 | 0 | 0 | 558 | 2000 |  |
| 4.1 | TSS with ESMS |  | 2000 |  |  | 58 | 2000 | Data acquisition form SM-160 |
| 4.2 | Facilities without ESMS |  | 500 |  |  | 500 |  | Non-reconstructed TSSs |
|  | TOTAL |  | 2817 | 168 | 46 | 600 | 2000 |  |

* - At this stage of the technical readiness of the facility, the ACS TP (TM) equipment installed within the framework of these works must ensure only the transmission of teleinformation. In the future, during the reconstruction of the primary and secondary equipment, the installed ACS TP (TM) equipment without replacement must be able to ensure full-fledged remote control (RC) and digital integration of the RP&A MPT.

** to perform the work provided for in this paragraph, it is necessary to install a controller that will have the appropriate number of dry contacts to ensure that signals of the presence or loss of voltage from the input and/or 0.4 kV directions are sent to the main server, as well as data from the meters installed in the substation.

ANNEX  2. Short list of information  received from automation facilities of  CJSC «ENA»

Typical list for 110 – 35 kV SSs

It is necessary to provide RS: - Position of switching devices 110, 35, 6(10)kV: - Switches - Disconnectors - Earthing blades - Isolators - Short-circuiters - Position of movable elements in the complete switchgear. - Position of the on-load tap changer of transformers. - Position of keys and control switches for relay protection and automation (RPA) and anti-emergency automation. - Emergency-warning telecommunication signaling (EPTS). - All signals involved in the relay protection and automation (RPA) terminals.. - Fire and security alarm signals (if available). - Position of switching devices of the ODC (operational direct current) and AP (auxiliary power) systems. It is necessary to ensure the following telemetry (TM): - Phase currents, total active and reactive power at the connections: - High-voltage lines 110 and 35 kV, - Transformer inputs on the 110, 35, 6(10) kV side, - Sectional, busbar, and bypass switches, - 6(10) kV feeders, - Line voltages, network frequency at all busbar sections. - Voltages at the ODC and AP busbars. - Power factor cosφ. - Oil temperature of transformer equipment. It is necessary to provide the following RC : - 110, 35, 6(10) kV switches. - 110, 35, 6(10) kV disconnectors equipped with drives for remote control. - Earthing blades (if technically possible). - Recording of settings in MP RPA terminals. If possible, creating a transparent mode for remote setting of MP RPA parameters.

Substation equipment and control

It is necessary to provide RS: - Opening the door of the ТМ Box. - Availability of ТМ Box voltage. - Status of doors in SS premises (open/closed).

For facilities  of type 1.1, obtaining the specified volume of teleinformation is performed by polling the existing ACS TP system. Expansion of the volume of information collected by the ACS TP is performed by “ENA” CJSC

For facilities of type 1.2, 1.3, 2.2 and 2.3 new ACS TP is under creation in accordance with the list presented in this Annex.  The volume of information collected by the ACS TP is determined by the technical readiness of the existing substation equipment.

6 (10) kV SP, type 3.2.1 and 3.2.2

It is necessary to provide RS: - Position of switching devices 6(10)kV: - Switches - Disconnectors - Earthing blades - Isolators - Short-circuiters - Position of movable elements in the complete switchgear. - Position of keys and control switches for relay protection and automation (RPA) and anti-emergency automation. - Emergency-warning telecommunication signaling (EPTS). - All signals involved in the relay protection and automation (RPA) terminals.. - Fire and security alarm signals (if available). - Position of switching devices of the ODC (operational direct current) and AP (auxiliary power) systems. It is necessary to ensure the following telemetry (TM): - Phase currents, total active and reactive power at the connections: - Inputs on the 6(10) kV, - Sectional, busbar, and bypass switches, - 6(10) kV feeders, - Line voltages, network frequency at all busbar sections. - Voltages at the ODC and AP busbars. - Power factor cosφ. - If the MT RPA terminal does not provide voltage data, it should be obtained directly from the voltage transformers by installing digital measurement converters directly on the incoming cells, and the remaining parameters will be calculated in the SCADA system. It is necessary to provide the following RC : 1. 6(10) kV switches. 2. 6(10) kV disconnectors equipped with drives for remote control. 3. Earthing blades (if technically possible). 4. Recording of settings in MP RPA terminals. If possible, creating a transparent mode for remote setting of MP RPA parameters.Необходимо обеспечить ТУ:

Equipment and control

It is necessary to provide RS: - Opening the door of the ТМ Box. - Availability of ТМ Box voltage. - Status of doors in SS premises (open/closed).

The volume of teleinformation collected by the ACS TP (TM) is limited to the information that can be collected from the MPT RP&A. This title does not provide for the installation of additional devices in 6-10 kV cells, except for what is indicated above.

SP 6 (10) kV, Type 3.3

It is necessary to provide RS for input sell : - Status of switches It is necessary to provide the following remote measuring- telemetry (TM) - current of phases A, B, C - line voltages АВ, ВС, СА - Total, active and reactive power P, Q - Frequency

Linear and Section Cells

It is necessary to provide RS fot Linear and Section cells : - Status of switches

Substation equipment and control

It is necessary to provide RS : - Opening TM Box doors; - Opening SP doors. - Presence of voltage in the TM Box.

6 (10) kV TSS, Type 4.1

Input cell 0,4 kV

It is necessary to provide RS : - Presence of voltage on the busbars 0,4 kV It is necessary to provide TM (provided by polling SM-160-02M): - voltage and current of phases A, B, C - Total, active and reactive power P, Q - Power factor cosΦ - Frequency

Substation equipment and control

It is necessary to provide RS : - Opening TM Box doors (if available); - Opening TSS doors*.

6 (10) kV TSS, Type  4.2

Input cell 0,4 kV

It is necessary to provide RS : - Presence of voltage at inputs and directions (on average 4 in each TSS) 0.4 kV, It is necessary to provide TM (provided by polling the meters if SM-160-02M is installed): - voltage and current of phases A, B, C - Total, active and reactive power P, Q - Power factor cos Φ - Frequency

2. Substation equipment and control

It is necessary to provide RS : - Opening TM Box doors; - Opening TSS doors.

# Annex 3. Typical structural diagrams